## Slide 1
Bernardo Ferreira
Supervisor: Prof. Dr. João Paulo Barraca
Co-supervisor: Mestre Nuno Lourenço
Examiner: Prof. Dr. Jorge Sá Silva
Dissertação de Mestrado Integrado em Engenharia de Computadores e Telemática
Aveiro, 20 Dezembro de 2017
Building Automation with Failure Tolerance
Automação de Edifícios com Tolerância a Falhas

## Slide 2
Outline
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work
Notes: Estrutura
Introdução teorica
E finalmente as conclusoes e trabalho futuro

## Slide 3
Motivation & Objectives
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work

## Slide 4
Problems
Motivation & Objectives
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Non-residential buildings take a huge part of the worldwide energy consumption;
Building Automation Systems solutions are very expensive;
Most of the solutions are proprietary and therefore, the hardware, installation and management is controlled by the same vendor.
Notes: Nos dias que correm e com base em varios estudos cncluiu-se que os edificios não residencias consomem uma grande quantidade de energia.
Um dos grandes problemas de soluçoes para smart buildings é o preço e serem proprietarios, ou seja a empresa controla desde o hardware à instalação e gestão.

## Slide 5
Motivation
Motivation & Objectives
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
IT2 building lack the support for intelligence and automation systems;
Reduce operational costs while increasing comfort of IT2 building occupants.
Notes: Falta de uma solução de automaç\ao da climatizaç\ao, luzes etcc no IT2
E tambem a redução dos custos operacionais e aumento do conforto dos seus ocupantes.

## Slide 6
Objectives
Motivation & Objectives
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Enhance SmartLighting project with new features:
  Remove single points of failure;
  Detect system failures and react fast to resolve them;
  Empower gateways with event processing capabilities.
Notes: Os objectivos para este trabalho foram:
  Melhorar o projeto SmartLighting removendo pontos unicos de falha
  Deteção automatica de falhas nos componentes e capacidade para as resolver
  Adicionar às gateways capacidade de processamento de eventos.

## Slide 7
Framework
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work
Notes: Breve introdução teorica

## Slide 8
Building Automation Systems
Framework
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Automate HVAC, Lighting etc.;
Intelligent energy management;
Main goal: Lower energy costs and reduce building’s sector energy footprint;
Main market competitors: Honeywell, Siemens, Schneider Electric, Johnson Controls;
Protocols: KNX, BACnet, LonWorks, EnOcean.
Notes: Automação de edificios.
Automatizar a climatização, iluminação etc, fazendo uma gestao inteligente da energia de modo a reduzir os custos operacionais dos edificios
Alguns protocolos usados
Mais recentemente o fenomeno da internet das coisas tem vindo a revolucionar o mercado, tendo estes vendedores de se adaptar.

## Slide 9
Complex Event Processing
Framework
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Derive conclusions from tracking and processing streams of information in real-time;
Drools Fusion, Esper, WSO2 Siddhi.
Notes: Correlacionar grandes quantidades de dados de modo a produzir respostas baseadas em regrass e padroes pre definidas ou eventos passados

## Slide 10
Fault Detection Techniques
Framework
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Ping messages or Heartbeat messages;
Centralized or distributed approach.
Centralized fault detection
Distributed fault detection using Heartbeat
Notes: mudar imagens

## Slide 11
SmartLighting Project
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work

## Slide 12
Overview
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Aims to create a smart environment in IT2 building;
Automation of HVAC and lighting infrastructure;
Act in real-time based on collected data;
Allow setting up rules based on user’s preferences;
Building management platform
Moreira, H. “Sensor Data Integration and Management of Smart Environments.” 2016.
Notes: Atuar em tempo real aos dados lidos nos sensores
Disponibilizar a criação de regras de automação aos utilizadores e gestores do edificio

## Slide 13
Global Architecture
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work

## Slide 14
Global Architecture
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Building Management:
User friendly platform;
Rule management;
Distribution of devices in a virtual building’s schema.

## Slide 15
Global Architecture
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
CEP Engine:
High performance WSO2 CEP Engine;
Process sensor events based on the implemented rules.

## Slide 16
Rules Standard
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Light 1
Sensor 1
Sensor 2
Light 1
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Notes: caracteriza a localizaçao do dispositivo no edificio

## Slide 17
Global Architecture
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Message Broker:
Message-oriented middleware;
MQTT Protocol;
Publish/Subscribe model;
Notes: Broker de mensagens
Elemento por onde todos os componentes comunicam
Utiliza o protocolo MQTT
Utiliza metodo de Publish/Subscribe

## Slide 18
Global Architecture
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateway Manager:
Rules and devices distribution;
Awareness of Gateway’s state;
Resolve Gateway’s failures.

## Slide 19
Global Architecture
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateway:
Convert sensor events to understandable messages and vice-versa;
Process events using a lightweight CEP engine.

## Slide 20
Operational Scenarios
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 1 - All components are operational
Scenario 2 - CEP Engine failure

## Slide 21
Operational Scenarios
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 3 – Gateway Manager Failure
Scenario 4 – Gateway Manager and CEP Engine failure

## Slide 22
Operational Scenarios
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 5 – MQTT Broker failure

## Slide 23
Implementation
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work

## Slide 24
Architecture
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Notes: tecnologias existentes

## Slide 25
Gateway Manager
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Implemented using Python 3 and the Eclipse Paho MQTT Python client library.
Implemented Features:
Rule Parsing and Distribution;
System Awareness;
Devices configuration;
Gateway Manager Dashboard;
Gateway Failure Handling;
Gateways Synchronization.
Notes: Tirar implemented featurees

## Slide 26
Gateway Manager
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Rule Parsing and Distribution:
Receive rules from the Building Management, parse and divide the JSON into sub rules;
Distribute sub rules to available Gateways using a round-robin method.
Devices Configuration:
When a gateway connects to the system, publishes the devices within its range;
Balances and distribute the devices among the available gateways;
Uses a round-robin method.
Notes: gm features

## Slide 27
Gateway Manager
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
System Awareness:
Subscribe to every component heartbeat MQTT topics;
Periodically checks if every component has sent the heartbeat message;
After 10 seconds without receiving an heartbeat from some component, begins implementing failure handling measures.
Gateway Failure Handling:
Checks which gateways have the lost devices within its range;
Distribute and inform gateways to take over those devices;
Redistribute rules among available gateways.
Notes: mudar 4 ponto

## Slide 28
Gateway Manager
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateways Synchronization:
Sends to gateways information regarding which rules and devices are controlled by each gateway.
Useful in Scenario 5.

## Slide 29
Gateway Manager
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateway Manager Dashboard:
Implemented using Flask;
Information about each gateway’s state;
Turn gateways on/off;
List of rules and its locations;
List of devices and which gateways control them;

## Slide 30
Gateway
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Implemented using Micropython.
Avahi Multicast mDNS deamon.
Implemented Features:
Devices Configuration and Management;
Rule Parser;
Gateway Automation Engine.
Notes: Micropython:
- Implementação eficiente do Python3 com apenas um subset da biblioteca de python. Otimizado para correr em microcontroladores

## Slide 31
Gateway
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Devices Configuration and Management:
Gateways report available devices when connected;
The BM and GM respond with device’s publish topics;
Gateways subscribe to its device’s topics in the MQTT Broker;
Gateways start publishing events to the corresponding topics.
Rule Parser:
Parse sub rule sent by the Gateway Manager;
Create objects for each action specification;

## Slide 32
Gateway
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateway Automation Engine:
Function:
  Set Value;
  Set Percent;
Filter:
  =, !=, >, <, >=, <=;
Window:
  Time Window;
  Length Window;
Aggregator:
  Average;
  Any
  None
Converter:
  Lux to Percent;
  Set 1, Set 0;
Notes: Implementadas janelas temporais
Janela de numero de eventos
Usadas com agregadores
Media, retorna 1 se um valor na window >1
Retorna 1 Se forem todos zero
Intensidade luminosa para percentagem
Colocar a um ou a 0

## Slide 33
Gateway
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Check to which actions the event apply;
Process and send values to the target topics.
Gateway Automation Engine:

## Slide 34
Operational Scenarios
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 1 - All components are operational
Gateways publish device events;
CEP Engine process events;
Gateway failure handling operational.
Notes: Gateway – Broker - Cep
Gateways têm tolerancia a falhas

## Slide 35
Operational Scenarios
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 2 - CEP Engine failure
Gateways publish device events;
Gateway’s automation engine process events;
Gateway failure handling operational.
Notes: Gateway – Broker - Gateway

## Slide 36
Operational Scenarios
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 3 – Gateway Manager Failure
Gateways publish device events;
CEP Engine process events;
Gateway failure handling disabled.
Notes: Gateway – Broker – CEP
Gateways nao podem falhar

## Slide 37
Operational Scenarios
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 4 – Gateway Manager and CEP Engine failure
Gateways publish device events;
Gateway’s automation engine process events;
Gateway failure handling disabled.
Notes: Gateway – Broker – Gateway
GW nao podem falhar

## Slide 38
Operational Scenarios
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Scenario 5 – MQTT Broker failure
Gateways publish device events directly to other gateways;
Gateway’s automation engine process events;
Gateway failure handling disabled.
Notes: Gw – Gw
Nao há resolução de falhas

## Slide 39
Evaluation & Results
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work

## Slide 40
Deployment Scenario
Evaluation & Results
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Deployment in IT Building internal network.
Virtual machine with Gateway Manager software and dashboard.
Virtual machine with Building Management.
Virtual machine with WSO2 CEP.
Mosquitto MQTT Broker.
Two Raspberry Pi 3 as Gateways.
Notes: Virtula machines:
  xxx
  xxx
  xxx
  xx

## Slide 41
Performance Results
Evaluation & Results
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateway Automation Engine Performance
Stress test:
  Measure the time to process 1, 10, 100, 1000 and 10000 consecutive events.
  10 runs each.
Notes: Medido o tempo desde o envio do primeiro evento até a receção da ultima resposta

## Slide 42
Performance Results
Evaluation & Results
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Chart: Performace of Gateway's Automation Engine
| 1.0 | 10.0 | 100.0 | 1000.0 | 10000.0
Processing time of each event | 5.1891 | 5.8597 | 4.5526 | 5.3498 | 5.7953
Time to process all events | 0.0051891 | 0.058597 | 0.45526 | 5.3498 | 57.9533
Average of 4 to 6 ms to process a single event.
CPU usage:
  Idle: 1 core 100%
  10000 events: 100% core 1
        16% core 2
Notes: previsivel
Idle a 100 por causa do event loop do micropython.
Não suporta threads

## Slide 43
Performance Results
Evaluation & Results
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Gateway Reaction Time
Reaction time to a failure in the CEP Engine.
  Disable the CEP Engine.
  Measure the time needed for a Gateway to start processing events.
Reaction time to a Gateway Failure.
  Two Gateways with the same devices sending heartbeats in 5 second intervals.
  Disable Gateway 1.
  Measure Gateway’s 2 reaction time and later Gateway’s 1 recovery time.
Notes: Por os intervalos em cima

## Slide 44
Performance Results
Evaluation & Results
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Failure in the CEP Engine.
Gateways wait 5 seconds before conclude that the CEP Engine is unreachable
10 runs.
Average of 7.3 sec of reaction time.
Notes: cep envia um em um sec

## Slide 45
Performance Results
Evaluation & Results
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Reaction to a failure.
10 runs.
Average of 13.2 sec of reaction time.
Recovery from a failure.
10 runs.
Average of 164 ms of recovery time.
Notes: Desde que a GW é desligada,
Até os seus despositivos serem controlados por outra gateway
GW 5 em 5 a mandar para o GM
GM 10 em 10 a verificar se falhou

## Slide 46
Conclusion & Future Work
Motivation & Objectives
Framework
SmartLighting
Project
Implementation
Evaluation & Results
Conclusion & Future Work

## Slide 47
Conclusion
Conclusion & Future Work
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
The proposed objectives were achieved;
Failure handling of different operational scenarios;
Modular and lightweight solution.
Some problems found:
  Handle of Gateway’s failures dependent on the Gateway Manager’s state;
  Micropython’s limitations.
Notes: Micropython ter algumas limitaçoes e nao ter sido feita uma implementação mais eficiente.
Falha num componente consegue ser remediada com o minimo de consequencias para os ocupantes

## Slide 48
Future Work
Conclusion & Future Work
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Persistence;
Security;
Implement service discovery in Gateways;
Extend Gateway’s Automation Engine modules.

## Slide 49
Bernardo Ferreira
Supervisor: Prof. Dr. João Paulo Barraca
Co-supervisor: Mestre Nuno Lourenço
Examiner: Prof. Dr. Jorge Sá Silva
Dissertação de Mestrado Integrado em Engenharia de Computadores e Telemática
Aveiro, 20 Dezembro de 2017
Building Automation with Failure Tolerance
Automação de Edifícios com Tolerância a Falhas

## Slide 50
Fault Recovery Techniques
Framework
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Hot standby redundancy.
N Modular redundancy.
Notes: tiro

## Slide 51
References
[1] Moreira, H. “Sensor Data Integration and Management of Smart Environments.” 2016.

## Slide 52
Hardware Device
Framework
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Raspberry Pi 3 Model B;
Quad Core 1.2GHz 64bit ARM CPU;
1GB RAM;
Others: Nano Pi, VoCore, CloudBit etc..
Gateway hardware
Notes: tirar

## Slide 53
Requirements
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Fast Responsiveness;
Flexibility;
Scalability;
Failure Handling and Basic Functionalities;
Data Correlation;
User Control and User-Friendly Interfaces.

## Slide 54
Gateway
Implementation
Building Automation with Failure Tolerance
Bernardo Ferreira
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work
Rule Parser:
Parse sub rule sent by the Gateway Manager;
Create objects for each action specification;
Notes: Este para a frente
tirar

## Slide 55
Access to Devices
SmartLighting Project
Building Automation with Failure Tolerance
Bernardo Ferreira
IP Smart Objects Alliance Guidelines
Each Device can have multiple objects.
Each Object can have multiple Resources.
Access URI:
/Building/Floor/RoomType/Room/Area/Device/Obj.ID/Obj.Instance/Res.ID/Res.Instance
Motivation & Objectives
Framework
SmartLighting Project
Implementation
Evaluation &
Results
Conclusion &
Future Work